## Slide 1: Shipboard Power System Characteristics Shipboard Power System Fundamentals Revision of 20 December 2025
Dr. Norbert Doerry
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2025 by Norbert Doerry This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Essential Questions
What is electrical power used for onboard ship? | Understand
What are the implications of a need for high power reliability / Quality of Service? | Understand
What are the implications of a need for survivable power systems? | Understand
What are the implications of the marine environment? | Understand

## Slide 3: Uses of electrical power onboard ship
IEEE Std 45.1
    100 Propulsion
    200 Batteries and battery chargers
    300 Power conversion equipment
    400 Lighting
    500 Electronics
    600 Navigation systems
    700 Auxiliaries
    800 Heating ventilation and air conditioning systems
    900 Deck machinery
    1000 Food services
    1100 Workshops/Laundry equipment
MIL-STD-881
  100 Hull structure
  200 Propulsion plant
  300 Electric plant
  400 Command, communications, and surveillance
  500 Auxiliary systems
  600 Outfit and furnishings
  700 Armament
A ship is a floating city

## Slide 4: Power Quality – Quality of Service
Power Quality
  Power consistently adheres to interface standard
    MIL-STD-1399 section 300 part 1 (LVAC)
    MIL-STD-1399 section 300 part 2 (MVAC)
    IEEE Std 45.1 (all)
  Measured at the interface between power system and loads
    Similar to the point of common-coupling in terrestrial power systems
Quality of Service
  Mean time between service interruption (MTBSI)
  A service interruption is a power interruption that lasts longer than a load can tolerate
    Reconfiguration time (t1) is the maximum time to reconfigure the distribution system in response to a fault without bringing on additional generation capacity.
      Function of technology used in circuit protection devices.
    Generator start time (t2) is the maximum time to bring the slowest generator set (that can act as a standby generator set) online.
  Loads categorized by tolerance to power interruptions
    Uninterruptible – cannot tolerate power interruptions of duration t1.
    Short term interrupt – can tolerate power interruptions of duration t1, cannot tolerate power interruptions of duration t2.
    Long term interrupt – can tolerate power interruptions of duration t2.

## Slide 5: Characteristics of shipboard power systems (As compared to terrestrial systems)
Frequency is not a constant
Lack of time scale separation
Load sharing instead of power scheduling
Short electrical distances
Load dynamics may be important
Tighter control
Ungrounded or high-resistance grounded systems
Physical environment

## Slide 6: Survivability
Threats
  Collision
  Flooding
  Fire
  Cyber attack
  Weapons detonation (naval ships only)
Susceptibility
  Likelihood that the electrical power system will be exposed to a threat
Vulnerability
  How well the electrical power system maintains power quality and power continuity following exposure to a threat
Recoverability
  How quickly electrical power can be restored following an outage caused by a threat.

## Slide 7: Survivability requirements
Commercial ships
  Regulations (law)
  International Treaties such as SOLAS
  Classification Societies (such as ABS, DNV, LR)
Complex ships – Zonal Design
  Ship is divided into multiple zones
    Zone boundaries align with the hull and watertight subdivision bulkheads
    Same zone boundaries apply to all distributed systems.
  Zonal Survivability
    Damage to one or two adjacent zones does not result in a service interruption in undamaged zones. (May only apply to mission critical equipment)
    Addresses Vulnerability
  Compartment Survivability
    Power can be quickly restored to mission critical equipment in a damaged zone if it is same to do so.
    Addresses Recoverability
    May incorporate a casualty power system

## Slide 8: Marine Environment
Characteristics
  Ship motions (roll, pitch, slam, list, trim, etc.)
  Atmosphere (extreme temperature variation, high salt, high humidity)
  Vibration
  Damaging fumes or vapors
  Abrasive particles
  Salt spray
  Ice
  Sunlight
  Shock and blast (naval ships)
Standards
  IEEE Std. 45.1
  MIL-DTL-917 Basic Requirements
  MIL-DTL-901 Shock Tests
  MIL-STD-167-1 Mechanical Vibrations
  MIL-STD-1399-301 Ship Motion and Attitude
  MIL-STD-1399-302 Weather Environment