## Slide 1: Shipboard Power System vs Terrestrial Power Systems Shipboard Power System Fundamentals Revision of 21 December 2025
Dr. Norbert Doerry
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2025 by Norbert Doerry This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Essential Questions
What are the implications of differences in power management and system control techniques? | Understand
What are the implications of differences in fault management techniques? | Understand
What are the implications of differences in cable lengths? | Understand
What are the implications of differences in load management techniques? | Understand

## Slide 3: Differences between Shipboard Power Systems and Terrestrial Power Systems
Non-constant frequency
Lack of time scale separation
Load sharing instead of power scheduling
Short electrical distances
Load dynamics
Tighter control
Ungrounded or high-impedance grounded systems
Physical environment

## Slide 4: Power management and system control
Terrestrial power systems
  System has “infinite” inertia.
    Frequency and voltage controlled to very close tolerances
  Generator sets scheduled with respect to power provided.
  Voltage setpoints set to keep voltages and reactive power within bounds.
  Some transformers have tap changers which can be used to keep voltages within bounds.
  System power factor can be managed with capacitors and static VAR compensators.
  Determining which generators to have online is based on ongoing optimization calculations
  Bringing online a new generator can take hours
Shipboard power systems
  System has limited inertia.
  Select loads may be a significant fraction of online generator set capacity.
    Can cause significant voltage and frequency transients
  Using droop to share real and reactive power can result in the frequency and voltage deviating from nominal values.
  Optimal line-ups of generator sets determined during design
  Bringing online a new generator can take seconds to minutes

## Slide 5: Fault management
Terrestrial Power Systems
  Solidly grounded
    Line to line and line to ground faults result in large currents used with coordinated breakers to clear faults
  Many faults are self clearing
    Automatic attempt to reclose after a few seconds
  Long cables limit fault current
Shipboard Power Systems
  High Impedance or ungrounded
    Line to line faults result in large currents used with coordinated brakers to clear faults
    Continued operation with single line to ground faults
  Most faults are not self clearing
  Short cables result in high fault currents
    Nominal system voltage often based on matching available fault current from generators with fault interruption capability of circuit breakers.
    Rating of medium voltage to low voltage transformers may be limited based on fault current.

## Slide 6: Cable lengths
Terrestrial Power Systems
  For many analyses, generator sets are assumed to be in parallel with an infinite grid via the impedance of a long cable
Shipboard Power Systems
  Smaller impedance of shorter cables results in tighter coupling of the dynamics of paralleled generator sets
    Analyses should account for the coupling among all paralleled generators
    Large power fluctuations among the paralleled generators can occur during transients.
      May be large enough to trip generator sets offline

## Slide 7: Load management
Terrestrial Power Systems
  Large number of generator sets online
    Loss of any one does not impact ability of system to serve all loads
Shipboard Power Systems
  Only a few generator sets online
    Loss of any one may impact ability of system to serve all loads
  Relies on load shedding to keep the total load less than online generation capacity.
  Large loads should coordinate with power management system before making a large change in load.
    Examples include propulsion motors, and large ventilation fans