## Slide 1: Power Generation Shipboard Power System Fundamentals Revision of 7 January 2026
Dr. Norbert Doerry
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2026 by Norbert Doerry This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Essential Questions
What prime movers are used onboard ship and why? | Understand
What components comprise Power Generation? | Remember
What fuels do the prime movers use and why? | Understand
How is the fuel rate calculated using an sfc curve? | Apply

## Slide 3: Introduction
Power Generation
  Converts energy (not of electrical origin) into electrical energy.
  Source of energy is typically chemical in the form of “fuel”
  Other sources of energy
    Steam (thermal)
    Waste heat (thermal)
    Solar (radiation)
    Wind (kinetic energy)
Generator Set
  Most common implementation of Power Generation
  Prime mover (usually gas turbine or diesel engine)
  Synchronous generator
  Supporting auxiliaries and controls
Uncommon implementations of Power Generation
  Fuel cells
  Photovoltaic systems
  Waste heat systems
  Wind turbines

## Slide 4: Prime Movers
Diesel Engines
  Tend to be large and heavy
    Usually located low in ship
  Good fuel efficiency
  Often used to satisfy endurance conditions
Gas Turbines
  Smaller and lighter than diesel engines
    Usually located low in ship, but may be located higher in ship.
  Not as good fuel efficiency as diesel engines
  May be used to achieve sustained speed conditions
    If significantly higher power levels than endurance conditions
  May employ reduction gear to reduce high shaft speed of gas turbine (>3000 rpm) to 1800 rpm to enable use of 4 pole synchronous generator for 60 Hz operation.

## Slide 5: Generator Set Components
Engine (prime mover)
  Diesel or Gas Turbine typical.
Synchronous generator
  For 60 Hz output, RPM is a sub-multiple of 3600 (1800 and 1200 rpm are common).
    May require gearbox for gas turbine
  Higher frequency (200 to 300 Hz) output desirable for direct conversion to d.c.
Subbase
  Rigid structure for other components.
  Enable construction, alignment and testing before installation.
Voltage regulator
  Controls excitation current in the field winding of the synchronous generator to regulate the output voltage.
Speed governor
  Regulates the shaft speed of the prime mover and generator by controlling the fuel rate into the prime mover.
Starter
  Provides the mechanical means to start the engine.
  Example technologies include air motors and electrical motors.

## Slide 6: Generator Set Components (Continued)
Air Intakes and exhaust
  Air intakes provide combustion air and cooling air.
    Can include a cooling air fan.
  Exhaust conveys combustion products and heated air to the exterior of the ship.
Fuel system
  Day / Service Tank.
  Filters and water separators.
  Fuel pumps.
Cooling system
  Engines are typically cooled by oil or fresh water (with glycol).
    Seawater – oil or Seawater-freshwater heat exchanger transfers heat to the exterior of the ship.
  Generators often Totally Enclosed Water – Air cooled (TEWAC).
    Air cools the generator.
    Seawater – air heat exchanger cools the air.
Monitoring and Control System
  Coordinates generator set components.
  Communicates with external systems.
Rectifier (d.c. output only)
  Creates d.c. voltage for integration into d.c. power systems.

## Slide 7: Fuel Cells
Advantages
  Clean exhaust – reduce or eliminate NOX, CO2, SOX, and particulate emissions
  High efficiency
  Modularity
  Low noise and vibration
Disadvantages
  Traditional fuels (F76 or MGO) cannot be directly used – must be reformed
  Slow dynamic response to transients
    Usually require additional energy storage to support required dynamics
  Limited industrial base

## Slide 8: Fuel Cell Components
Fuel cell stack
Power converter
Fuel reformer
Supply air
Temperature and humidity control
Exhaust system
Monitoring and control system

## Slide 9: Photovoltaic Systems (Solar Panels)
Convert light directly into electricity
Amount of power and energy produced is usually not large
  Augment, rather than replace other sources of power and energy
  Special purposes

## Slide 10: Photovoltaic System Components
Solar Panels
  Typically contains a series and parallel network of solar cells.
  Power production depends on:
    Cleanliness of panels.
    Intensity of light.
    Angle between the normal angle of the panel with respect to the sun.
Maximum Power Point Tracker Converter
  Imposes a voltage on the solar panels to maximize the power produced.
Power System Interface Converter
  Converts power from the maximum power point tracker converter to the type of power needed by the power system.
  May not be needed if the power from the maximum power point tracker converter meets the applicable interface requirements.

## Slide 11: Fuel
Heavy Fuel Oil (HFO)
  Remains after crude oil refined has removed lighter components
  High viscosity – must be preheated
  Inexpensive
  May require special scrubbing systems to meet environmental laws
Distillate Fuels (MGO and F76)
  Lower viscosity than HFO
  More expensive
  Easier to meet environmental laws
  F76 (and JP5) standard fuel for U.S. Navy
Blended Fuels (mix HFO and MGO)
  Viscosity lower than HFO – eliminates need for preheating
Biofuels
  Reduces emissions of SOX and CO2
  Limited shelf live (typically 1 year)
  May require engine modifications

## Slide 12: Fuel (Continued)
Liquid Natural Gas (LNG)
  Reduces emission of SOX and CO2
  Requires engines designed to run on LNG
  Requires special storage tanks
Methanol (CH3OH)
  Reduces emission of SOX and CO2
  Less impact to ship than LNG
  Requires engines designed to run on methanol
  Must address high toxicity and high flammability
Ammonia (NH3)
  Eliminates emission of SOX and CO2
  Requires engines designed to run on ammonia
  Must address high toxicity and high corrosiveness

## Slide 13: Specific Fuel Consumption (SFC) vs Fuel Rate
Specific Fuel Consumption
  Fuel Rate (kg/hr) divided by power delivered (kW)
  Units kg/kW-hr (or lbs/HP-hr , g/kW-s, etc.)
  Depends on fuel used and the operating point of the engine (power and shaft speed)
  Inversely proportional to the prime mover efficiency
  Relatively constant above about 50% Power
  SFC often provided for engines at a few data points
  Tends to infinity as one approaches idle power
    Idle fuel rate divided by 0 output power.
    SFC generally not good for directly modeling fuel rates at low power levels.
Fuel Rates
  For many engines, the fuel rate as a function of power delivered is nearly linear (with a y-intercept equal to the idle fuel rate)
  For given data points, better to interpolate based on fuel rate rather than SFC
    Usually have to convert SFC to a Fuel Rate, then perform linear interpolation

## Slide 14: Gas turbine engine map - sfc curve – fuel rate curve
If an engine map is available, plot the load line (shaft power vs shaft speed) on the engine map and interpolate sfc from iso-sfc line to produce sfc vs power curve.
Convert the sfc vs power curve to a fuel rate vs power curve.

## Slide 15: Diesel engine map – sfc curve – fuel rate curve