## Slide 1: Common-Mode fundamentals for Shipboard Power Systems Part 2 Common Mode Modeling
Dr. Norbert Doerry Dr. John Amy
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2025 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Common Mode Lumped Parameter circuit model
Goal is to create a simplified circuit model that only models the impact of CM currents.
  Gain an understanding of where CM currents will flow.
  Gain an understanding of the magnitude of CM currents and voltage.
  Gain an understanding of what mitigation methods are likely to be successful or not.
Works well if the combined DM-CM Model is generally symmetrical.
  The same impedances, etc. are present on each conductor.
  Asymmetry results in linkages between the DM circuit and the CM circuit.
Usually works well up to about 1 Mhz. At higher frequencies, the behavior of physical devices typically deviates from their lumped parameter models.
  Cables for example, behave as RF transmission lines.
  Many more parasitic elements become important.

## Slide 3: Commode Mode lumped parameter model of Parasitic Capacitance
Goal of CM modeling is to concentrate only on CM voltages (neutral voltages) and CM currents and eliminate elements of the circuit that do not impact the CM circuit solution.
Combined CM and DM model
CM only model

## Slide 4: Common Mode lumped parameter model of inline resistors

## Slide 5: Common mode lumped parameter model of wye connected resistors
If connection to Vn2 is left unterminated, then can eliminate the wye connected resistors from the CM circuit since no CM current will flow.

## Slide 6: Common Mode lumped parameter model of delta connected load or windings (without parasitic capacitances)
Anything connected in delta (without parasitic capacitances) (or line to line )can be eliminated because Kirchhoff's Current law when applied to the three nodes requires the sum of the currents entering the delta connected load (Common Mode Current) to equal zero.

## Slide 7: Most three phase transformers (without parasitic capacitances) may be eliminated in the Common Mode lumped parameter model.
The Common Mode current transfer ratio between the primary and secondary windings of a three-phase transformer are proportional to the turns ratio.
However, per Kirchhoff’s current law, transformer windings that are delta, or are wye with the wye point unterminated cannot have a common mode current in the cables connected to the winding.
Special cases
  Wye-wye transformers with the wye point on both the primary and secondary windings are terminated. CM current on one winding will be transformed to a CM current on the other – The CM currents on the power system on primary side are linked to CM currents on the power system on the secondary side.
  Wye-delta or delta-wye transformers where the wye point on the wye winding is terminated. The CM current on the wye-winding is transformed to a circulating current in the delta winding (no CM current on the cable connected to the delta winding). The CM currents on the power system on the delta side are not linked to the CM currents on the power system on the wye side.
Other than the special case of a wye-wye transformer with both the primary and secondary wye-points terminated, the CM circuit on the primary side is isolated from the CM circuit on the secondary side.
  Parasitic Capacitance between primary and secondary windings, or between windings and ground may link the CM circuits of the primary and secondary sides.

## Slide 8: Generator windings in common mode lumped parameter models (No parasitic capacitance)
Generator delta windings are generally eliminated because Kirchhoff’s Current Law prevents CM currents in the cable connected to the winding.
Generator wye-windings where the wye point is not terminated are generally eliminated for the same reason as for delta windings.
Generator wye-windings where the wye point is terminated should be modelled as a voltage source between the wye point and the neutral voltage of the cable connected to the wye winding.
  The voltage source should have magnitude equal to the average of the instantaneous voltages of the conductors in the cable connected to the wye winding with respect to the wye point; the triple-n harmonics manifest as a common mode voltage.
  For a “balanced” source, the average of the instantaneous voltages of the conductors in the cable connected to the wye winding with respect to the wye point is 0; the generator may be modelled as a direct connection between the neutral voltage of the cable connected to the wye winding and the wye point.

## Slide 9: Common mode lumped parameter model of components with Mutual Inductance
Cables and common mode chokes have significant Mutual Inductance that results in different inductance values for differential and common mode circuit models.
Will be the subject of a future presentation.
For more detail, see …
  Doerry, Islam, and Prousalidis, Design of Shipboard Power System Grounding/Earthing, Wiley IEEE Press, 2025.

## Slide 10: What’s difficult to model in a CM lumped parameter circuit model?
Asymmetry
  Series impedances
  Links the DM and CM circuits
Multiple current paths if path impedance not known well
  Can be hard to split the CM current among multiple paths

## Slide 11: Typical Common Mode Voltage Sources
Power Electronics – introduce asymmetry (function of time)
Wye connected sources with Triple-n harmonics
  Only matters if wye point is terminated
Ground faults
Series impedances that are not equal
Voltage sources as part of wye point termination

## Slide 12: Example 1:
Mixed Model
DM Model
CM Model
Can use the DM Model to produce the CM voltage source waveforms in the CM Model

## Slide 13: Example 2
Combined DM – CM model
Recommend Video for Experiment 11
20250402 cm rectifier.asc

## Slide 14: Example 2
Load Current
Common Mode Current
DC Bus Voltage
Common Mode Voltage (DC Neutral ref AC Neutral)
Combined DM – CM model

## Slide 15: Example 2: Separate, but linked models
DM Model
CM Model
DM model calculates
CM Voltage Source magnitudes

## Slide 16: Example 2:
Load Current
DM Model
Common Mode Current
CM Model
DC Bus Voltage
DM Model
Common Mode Voltage (DC Neutral ref AC Neutral)
DM Model

## Slide 17: Example 2
AC Bus neutral to ground voltage Combined CM-DM Model
AC Bus neutral to ground voltage
DM Model
AC Bus neutral to ground voltage DM Model
AC Bus neutral to ground voltage
CM Model

## Slide 18: CM modeling
CM currents can often be estimated using a CM model.
CM Voltage source magnitudes can often be determined from a DM only model.
The “simplified” CM model helps identify strategies for controlling CM Currents
  Modify CM impedance
  Decrease CM voltages