## Slide 1: Common-Mode fundamentals for Shipboard Power Systems Part 4 Common Mode Modeling Cables and CM chokes
Dr. Norbert Doerry Dr. John Amy
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2025 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Common Mode Lumped Parameter circuit model
Goal is to create a simplified circuit model that only models the impact of CM currents.
  Gain an understanding of where CM currents will flow.
  Gain an understanding of the magnitude of CM currents and voltage.
  Gain an understanding of what mitigation methods are likely to be successful or not.
Modeling devices with mutual inductance poses special challenges

## Slide 3: Models for Mutual Inductance
Differential Mode Model
Common Mode Model
The inductance value provided for cables is typically L – M which is appropriate for Differential Mode Models. It is not appropriate for CM models

## Slide 4: Common Mode Chokes
Common Mode Chokes are designed to maximize L and M as well as make L and M nearly equal.
  Maximize common mode impedance
  Minimize differential mode impedance.

## Slide 5: Calculating Cable inductances (unarmored cable)
The common mode impedance for a cable of n identical cables evenly spaced apart is given by:
The differential mode impedance for each conductor of this cable is given by
Where l is the cable length (m)
ρ and d in m
L and M in µH
For other configurations, see
Doerry, Norbert, Mohammed Islam, John Prousalidis, Design of Shipboard Power System Grounding / Earthing, IEEEPress – Wiley 2025
Grover, Frederick W., Inductance Calculations, Dover Publications, Inc., Mineola NY, 2009

## Slide 6: Impact of common mode current on radiated emissions (EMI) of cable
The magnetic field B (Tesla) of a long conductor at a distance of r (m) and with a current I (amps) is given by
Where = 4 ×10-7 H/m.
For large r, the magnetic fields of the conductors of a cable will
  Nearly cancel with differential mode currents (sum of the currents is zero)
  Add with common mode currents.
Although typically much smaller in magnitude than differential mode currents, common mode currents can contribute significantly to radiated magnetic fields.

## Slide 7: Wrap up