## Slide 1: Experiment 1
Delta-Delta Transformer – Balanced Operation
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
208V
40V
5.2 : 1
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω
Notes: Delta delta transformers are common shipboard
Today we will explore steady state characteristics in an ungrounded system
The components we will investigate are
three phase power supply
delta-delta transformer
parasitic capacitance to ground
wye-connected resistors for a neutral connection
delta connected load resistors

## Slide 3: Experiment 1
Wye
Parasitic
Delta
Primary - LL
Secondary - LL
Primary - Delta
Secondary - LN
Secondary - L
Secondary - Delta

## Slide 4: Simulation Model
20240727 experiment 1-nl.asc
LTspice XVII

## Slide 5: Three Phase Power Review
Balanced three-phase = waveforms with equal magnitude and frequency but phase shifted by 120 electrical degrees
The three waveforms sum to zero
Notes: Balanced three phase definition

## Slide 6: Three Phase Power Review
Peak value is times the root mean square (RMS) value

## Slide 7: Three Phase Power Review
Line to line voltage is times the line to neutral voltage
  Phase shift is radians (from Van) or 30 degrees
peak

## Slide 8: Three Phase Power Review
Real Power
After a lot of trigonometry ….
Convert from peak to rms values for both current and voltage
Convert from line to neutral voltage to line to line voltage
= Power Factor
Watts

## Slide 9: Transformer turns ratio is approximately the ratio of primary to secondary voltage

## Slide 10: Ratio of currents not exactly the turns ratio

## Slide 11: The neutral to ground voltage is zero for balanced operation
SA
SB
SC

## Slide 12: The sum of the currents through the parasitic capacitances is zero (in balanced operation)

## Slide 13: Current in Load Resistor
SA
SB
SC

## Slide 14: Line current into Delta resistive Load
=
SA
SB
SC

## Slide 15: Wrap up