## Slide 1: Experiment 10a
Wye-Wye Transformer – 4 wire Solidly Grounded System Unbalanced Load and Ground Fault
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω
RLa = 200 - 300 Ω Rlamp = 450 Ω
N = 2
RG = 400 Ω
Common Mode Current Probe
Current Meter (all phases)
Voltage Meter (all phases)
Rlamp
(Neglecting losses)

## Slide 3: Experiment 10
Wye
Parasitic
Wye-Load
Secondary - LL
Secondary - LN
Primary line
Secondary - LG
Load line
Secondary line

## Slide 4: Simulation Model
20241029 experiment 10a.asc
LTspice

## Slide 5: Steady State Voltages – Ground Fault / Unbalanced Load
Secondary Line to neutral Voltage: 60 V rms (85 V peak)
Ground Fault
Unbalanced Load

## Slide 6: Steady State line to ground Voltages – Ground Fault / Unbalanced Load
Ground Fault
Unbalanced Load
Loads on unfaulted phases experience 73% overvoltage during ground fault

## Slide 7: Neutral to ground voltage (CM Voltage) and CM Current through Parasitic Capacitances, lamp resistances, and grounding resistor
Neutral to Ground Voltage
CM Current through Parasitic Capacitances, Lamp Resistors, and Ground Connection
Ground Fault
Unbalanced Load

## Slide 8: Line currents into the wye load and into primary not balanced with unbalanced load
Current into
Wye load
Current into
Primary
Ground Fault
Unbalanced Load
Primary currents not extremely large during ground fault – may not trip fault protection

## Slide 9: Line Currents out of Transformer
Secondary currents not extremely large during ground fault – may not trip fault protection

## Slide 10: Ground faults and unbalanced load results in current in the Neutral Conductor
Ground Fault
Unbalanced Load

## Slide 11: Ground Fault Currents
Ground Fault
Ground fault current may not be
Sufficient to trip breakers

## Slide 12: Wrap Up