## Slide 1: Experiment 3
Delta-Delta Transformer – Ungrounded System Unbalanced Load
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω
RLa = 200 Ω Rlamp = 450 Ω
Common Mode Current Probe
Current Meter (all phases)
Voltage Meter (all phases)
Rlamp

## Slide 3: Experiment 3
Wye
Parasitic
Delta
Secondary - LL
Secondary - LN
Transformer line
Secondary - LG
Load line

## Slide 4: Simulation Model
20240810 experiment 3.asc
LTspice

## Slide 5: Line currents into the delta load not balanced with unbalanced load
Balanced Load Unbalanced Load

## Slide 6: Calculating the secondary line currents into delta load
If we generalize such that all the load resistors have different values, the line currents into the delta load are given by:
While the secondary line currents in the delta load resistors sum to zero, they are not necessarily 120° apart from each other.

## Slide 7: Line Currents on Primary are also not balanced with unbalanced load
Balanced Load Unbalanced Load

## Slide 8: Phase to Ground Voltages are not impacted by unbalanced load
Balanced Load Unbalanced Load

## Slide 9: Phase to neutral voltages are not impacted by unbalanced load
Balanced Load Unbalanced Load

## Slide 10: Line to Line voltages are not impacted by unbalanced load
Balanced Load Unbalanced Load

## Slide 11: No neutral to ground voltage (CM Voltage) or CM Current through Parasitic Capacitances or lamp resistances
Balanced Load Unbalanced Load
Neutral to Ground Voltage
CM Current through Parasitic Capacitances and Lamp Resistors

## Slide 12: Wrap Up