## Slide 1: Experiment 5
Delta-Wye Transformer – Ungrounded System Unbalanced Load
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω
RLa = 200 Ω Rlamp = 450 Ω
N = 5.2
Common Mode Current Probe
Current Meter (all phases)
Voltage Meter (all phases)
Rlamp
(Neglecting losses)

## Slide 3: Experiment 5
Wye
Parasitic
Delta
Secondary - LL
Secondary - LN
Primary line
Secondary - LG
Load line
Secondary line

## Slide 4: Simulation Model
20240831 experiment 5.asc
LTspice

## Slide 5: Steady State Voltages
Primary Line to Line Voltage: Peak = 294 volts
Secondary Line to Line Voltage: Peak = 98 V volts

## Slide 6: Line currents into the delta load not balanced with unbalanced load
Balanced Load Unbalanced Load

## Slide 7: Line Currents on Primary are also not balanced with unbalanced load
Balanced Load Unbalanced Load

## Slide 8: No neutral to ground voltage (CM Voltage) or CM Current through Parasitic Capacitances or lamp resistances
Balanced Load Unbalanced Load
Neutral to Ground Voltage
CM Current through Parasitic Capacitances and Lamp Resistors

## Slide 9: Wrap Up