## Slide 1: Experiment 8
Delta-Wye Transformer – 4 wire – Solidly Grounded System Unbalanced Load and Ground Fault
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω
RLa = 200 - 300 Ω Rlamp = 450 Ω
N = 5.2
Common Mode Current Probe
Current Meter (all phases)
Voltage Meter (all phases)
Rlamp
(Neglecting losses)

## Slide 3: Experiment 8
Wye
Parasitic
Wye-Load
Secondary - LL
Secondary - LN
Primary line
Secondary - LG
Load line
Secondary line

## Slide 4: Simulation Model
20240928 experiment 8.asc
LTspice

## Slide 5: Steady State Voltages – Ground Fault / Unbalanced Load
Secondary Line to Neutral Voltage: Peak = 56.6 V volts
Ground Fault
Unbalanced Load

## Slide 6: Steady State line to ground Voltages – Ground Fault / Unbalanced Load
Ground Fault
Unbalanced Load

## Slide 7: Neutral to ground voltage (CM Voltage) and CM Current through Parasitic Capacitances or lamp resistances
Neutral to Ground Voltage
CM Current through Parasitic Capacitances and Lamp Resistors
Ground Fault
Unbalanced Load

## Slide 8: Line currents into the wye load and into primary not balanced with unbalanced load
Current into
Wye load
Current into
Primary
Ground Fault
Unbalanced Load
Large currents during ground fault will activate over-current protection

## Slide 9: Line Currents out of Transformer
Large currents during ground fault will activate over-current protection

## Slide 10: Unbalanced load results in current in the Neutral Conductor
=94.3 mA peak
Ground Fault
Unbalanced Load
For unbalanced loads

## Slide 11: Current through Ground Connection
Ground Fault
Unbalanced Load
No current through the ground connection during an unbalanced load

## Slide 12: Ground Fault Currents
Ground Fault

## Slide 13: Wrap Up