## Slide 1: Experiment 9
Delta-Wye Transformer – 4 wire High Resistance Grounded System Unbalanced Load and Ground Fault
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω
RLa = 200 - 300 Ω Rlamp = 450 Ω
N = 5.2
RG = 400 Ω
Common Mode Current Probe
Current Meter (all phases)
Voltage Meter (all phases)
Rlamp
(Neglecting losses)

## Slide 3: Experiment 9
Wye
Parasitic
Wye-Load
Secondary - LL
Secondary - LN
Primary line
Secondary - LG
Load line
Secondary line

## Slide 4: Simulation Model
20240928 experiment 9.asc
LTspice

## Slide 5: Steady State Voltages – Ground Fault / Unbalanced Load
Secondary Line to Neutral Voltage: Peak = 56.6 V volts
Ground Fault
Unbalanced Load

## Slide 6: Steady State line to ground Voltages – Ground Fault / Unbalanced Load
Ground Fault
Unbalanced Load

## Slide 7: Neutral to ground voltage (CM Voltage) and CM Current through Parasitic Capacitances, lamp resistances, and grounding resistor
Neutral to Ground Voltage
CM Current through Parasitic Capacitances, Lamp Resistors, and HRG resistor
Ground Fault
Unbalanced Load

## Slide 8: Line currents into the wye load and into primary not balanced with unbalanced load
Current into
Wye load
Current into
Primary
Ground Fault
Unbalanced Load

## Slide 9: Line Currents out of Transformer

## Slide 10: Unbalanced load results in current in the Neutral Conductor
=94.3 mA peak
Ground Fault
Unbalanced Load
For unbalanced loads

## Slide 11: Ground Fault Currents
Ground Fault

## Slide 12: Wrap Up